## Slide 1: SINGLE DEPTH P2 HUMIDIFICATION PARTS LIST

## Slide 2: REMOVE CAPS FROM MOTORS

## Slide 3: ATTACH AB7770 SPRAYERS TO MOTORS. NOTE SPRAYER TO MOTOR ORIENTATION FOR PROPER TUBE ROUTING
P6433
P6269
SCREW ON (4)P6269 APPROXIMATELY 5mm ON TO STUD
PLACE AB7770 ON TOP OF NUTS
WRENCH TIGHTEN (4)P6433 NUTS TO TOP OF STUDS
WRENCH TIGHTEN P6269 UP TO BOTTOM OF PLATE
MOTOR 1
MOTOR 2

## Slide 4: DRILL 3/16”-4.5mm THROUGH ECU SIDE FRAME. (3 PLACES) USE AB7768 BRACKET AS HOLE MARKING TEMPLATE
MOUNTING HOLES FOR AB7768

## Slide 5: ATTACH AB7768 TO INSIDE OF ECU FRAME AS SHOWN

## Slide 6: TUBE ROUTING IN ECU FRAME (FAN ASS’Y REMOVED FOR CLARITY)
4mm BLACK
6mm WHITE
PB6098
B09032
4mm WHITE
AB8145
PT1233
PT1237
PT1235
PT6269
ADD (3) AB8145
TO SUIT

## Slide 7: TUBE ROUTING THROUGH FAN ASSY
SECURE TUBES TO MOTOR MOUNT
WITH CABLE TIE WRAPS

## Slide 8: MOUNT VALVE ASSEMBLIES IN CONSOLE
AB7767
AB7766
EXISTING MOUNTING HOLES IN CONSOLE PLATE

## Slide 9: DRILL HOLES THROUGH CONSOLE BACK
DRILL 7/8”-(23mm) THROUGH
DRILL 5/8”-(16mm) THROUGH
USE MB20547 AS HOLE TEMPLATE
DRILL 13/64”-(5mm) THROUGH (2 PLACES)
MB20547
P314

## Slide 10: TUBE ROUTING THROUGH BACK OF CONSOLE (HEATING COILS AND SUPPORT LEG REMOVED FOR CLARITY)
ECU SUPPORT LEG CROSS BRACE IN THIS AREA
ABOVE TUBE FITTINGS
PB6099
PB4833